## GAS SUPPRESSION
CLIENT: | SOUTH AFRICAN NATIONAL BIODIVERSITY INSTITUTE (SANBI)
PROJECT: | FIRE SUPPRESSION SYSTEM FOR THE SERVER ROOM IN THE ADMINISTRATION BUILDING AT THE KIRSTENBOSCH NATIONAL BOTANICAL GARDEN CAPETOWN
CONTRACT: | FIRE SUPPRESSION SYSTEM
Item No. | Description | Unit | Qty | Rate | Amount
A | NOVEC 1230 FIRE SUPPRESSION SYSTEM
1 | Supply and Install complete stand-alone NOVEC 1230 Gas Fire Suppression System for Server Room on Ground Floor Level one to be interfaced into the smoke detectors. 37sq.m with height of 3.65m
1.1 | 57.8Kg Modular Cylinder-Wall Mounted (25bar) | No. | 2 |  | 0
1.2 | NOVEC 1230 charge | kg | 115 |  | 0
1.3 | Pressure gauge w/switch 25 bar | Ea | 2 |  | 0
1.4 | 360deg 8 port nozzle . | Ea | 3 |  | 0
1.5 | Gas Control Panel Convetional including battery back up | Ea | 1 |  | 0
1.6 | 48 - 180Lt pipe kit | Ea | 2 |  | 0
1.7 | Detection devices complete with mounting bases/ sounders (Optical) | Ea | 2 |  | 0
1.8 | Flashing Beacon | Ea | 1 |  | 0
1.9 | System/ manual release sign | Ea | 1 |  | 0
1.1 | Upon device activation do not enter | Ea | 1 |  | 0
1.11 | Manual release device | Ea | 2 |  | 0
1.12 | Discharge hose 90 deg elbow L550mm ( for the system) | Ea | 2 |  | 0
1.13 | Container strap 48 litre (2 off) 462 | Ea | 4 |  | 0
1.14 | Steel pipe SABS approved Accessories
1.16 | Unions, Bends, equal Ts - to make a complete installation | Sum | 1 |  | 0
1.17 | Consumables | Item | 2 |  | 0
1.18 | Steel Pipe SABS approved 35mm | m | 15 |  | 0
1.19 | Fire cables and coundits for the fire detection system to make a complete installation | Sum | 1 |  | 0
1.2 | Interfacing Fire detection and Gas suppression system | Item | 1 |  | 0
1.21 | Electric Valve Actuator | Item | 2 |  | 0
| BALANCE BROUGHT DOWN |  |  |  | 0
| BALANCE BROUGHT FORWARD |  |  |  | 0
1.22 | Non Return Valve 35mm Steel | No. | 2 |  | 0
1.23 | Isolating Valves 35mm Steel | No. | 2 |  | 0
1.24 | Link Gas Suppression for the server room to Main Fire panel | Sum | 1 |  | 0
1.25 | 5 Kg CO2 Fire extinguisher and signage for the Server Office and Signage | Ea | 1 |  | 0
1.26 | All applicable signage to complete the installation and make it comply | Sum | 1 |  | 0
1.27 | Replace door with a fire fire rated door and ensure proper sealing | Ea | 1
1.28 | Make good all disturbed services during installation | Sum | 1 |  | 0
2 | PROJECT ENGINEERING AND QUALITY MANAGEMENT
Testing, balancing, commissioning and handover of Gas Suppression Installation including compilation of submitted to the Engineer for approval, and Gas installation certificate.
2.1 | Operation and Maintenance Instruction Manuals | Set | 4 |  | 0
2.2 | User Training | Item | 1 |  | 0
2.3 | Sets of "as built' drawings "including 1 cd" | Ea | 4 |  | 0
2.4 | 12 Months free maintenance | Item | 1 |  | 0
2.5 | Allow for 2 Inspections/ Service during the 12 Months Period | Item | 2 |  | 0
2.6 | Any other item neccesary that might have been omitted that might be necessary for completion of installation (please specify). | Item | 1 |  | 0
2.7 | Allow for Safety and Health Compliace | Item | 1 |  | 0
2.8 | Provide OSH certificate for compliance on Equipment system installed | Item | 1 |  | 0
2.9 | Additional Tests and Measurements as required by the engineer | Sum | 1 |  | 0
2.3 | Allow for transportation and travelling charges | Item | 1 |  | 0
| BALANCE BROUGHT DOWN |  |  |  | 0
| BALANCE BROUGHT FORWARD |  |  |  | 0
2.31 | Allow for site inspection and measurements for detailed production of shopfloor drawings | Item | 1 |  | 0
2.32 | Issuing of COC by a registered personal | Item | 1 |  | 0
2.33 | Provide a list of spare parts | Item | 1 |  | 0
2.34 | Provision of a Maintenance Control Plan | Item | 1 |  | 0
2.35 | Provision for the development of works program in liason with other services | Item | 1 |  | 0
2.36 | Any other Item the Tenderer Wishes to Add (Attach a schedule) | Item | 1 |  | 0
2.37 | Allow for the 3 year Maintenance of the system | Ea | 3
G | TOTAL CARRIED FORWARD TO TENDER SUMMARY PAGE |  |  | R