## BOQ
Item | Description | Unit | Qty | Rate | Amount
BILL 1: PRELIMINARY & GENERAL ITEMS
Fixed Items
1.1 | Allow for costs incurred for site establishment, ablution facilities, off-loading and storage and removal of site establishment on completion of contract. | Sum | 1
Time-Related Items
1.2 | Site supervision, site security and other relevant overhead costs | Sum | 1
1.3 | Allowance to attend to all site meetings and inspections, transport and time related to such meetings and inspections | Sum | 1
1.4 | Allow for Health And Safety File, including compliance with OH&S Act & Construction Regulations | Sum | 1
1.5 | Allowance for lifting gear, cranes etc. that may be required for moving plant & equipment into position | Sum | 1
1.6 | Allowance to comply, maintain all insurance premium costs,statutory contributions, provision of Sureties, Guarantee of Works, etc. | No | 1
1.7 | Other (Please Specify)
TOTAL CARRIED FORWARD TO SUMMARY PAGE
Item | Description | Unit | Qty | Rate | Amount
BILL 2: 110kVA STANDBY GENERATOR INSTALLATION
Diesel Generator Set
110kVA standby generator complete with a change over switch, AMF control panel, exhaust system, batteries, sound proof and weather proof canopy which will enable the set to stand outdoors on a concrete plinth. The set would produce 100kVA prime power at 0.8PF, 400/230V, three phase four wire, 50Hz running at 1500RPM. The fuel tank would be integral with the base and would contain sufficient fuel to run the generator for 12 hours running at full load. The generator set should come complete with all labels, notices and ancillary materials and equipment as required to complete the installation.
2.1 | Supply | No. | 1
2.2 | Install | No. | 1
2.3 | Construct concrete plinth for mounting the generator. Rate to include design and detailing of the plinth with oil trap to prevent oil spill and bund walls. | Sum | 1
2.4 | Earthing of the generator as per the SANS regulations | Sum | 1
Armoured Cables and ABC Conductor
600/1 000V PVC/PVC/SWA/PVC multi-core copper cable to SANS 1507-3 installed on cable tray, cable ladder, ground and sleeves including all fixings and accessories (cable trays and sleeves measured elsewhere)
70mm² 3-core + insulated neutral Aerial Bundled Conductor (ABC) with carbon- loaded XLPE 600/1000V to SABS 1418
2.5 | Supply | m | 170
2.6 | Install | m | 170
16mm² 4-core
2.7 | Supply | m | 40
2.8 | Install | m | 40
TOTAL CARRIED FORWARD
Item | Description | Unit | Qty | Rate | Amount
BROUGHT FORWARD
Cable Terminations
Make off and terminate the LV cable, complete with glands, lugs and shrouds including connection of cable to equipment terminals. Rate to include supply, nuts, flat and spring washers and any other accessories required to make task complete
70mm² 3-core + insulated neutral Aerial Bundled Conductor with carbon- loaded XLPE
2.9 | Supply | No | 3
2.1 | Install | No | 3
16mm² 4-core
2.11 | Supply | No | 2
2.12 | Install | No | 2
Earth Conductors
Bare Copper Earth Wire (BCEW)
35mm² BCEW
2.13 | Supply | m | 170
2.14 | Install | m | 170
16mm² BCEW
2.15 | Supply | m | 40
2.16 | Install | m | 40
Earth Conductors Terminations
Make off and terminate Bare Copper Earth Wire (BCEW), including lugs and connections.
35mm² BCEW
2.17 | Supply | No | 3
2.18 | Install | No | 3
16mm² BCEW
2.19 | Supply | No | 2
2.2 | Install | No | 2
Poles
Plant poles and backfill
9m 140-160mm pole top diameter poles
2.21 | Supply | No | 3
2.22 | Install | No | 3
Joints
2.23 | Supply and install a joint for 70mm² 3-core + insulated neutral Aerial Bundled Conductor and the existing PVC SWA cable | No | 1
TOTAL CARRIED FORWARD TO SUMMARY
Item | Description | Unit | Qty | Rate | Amount
BROUGHT FORWARD
Digging Holes for poles & stays and Excavations
Excavate for cable and sleeve trench including temporary support of sides, keeping excavations dry, backfilling and compacting as required.
2.24 | 9m pole hole & Stays (1.5m deep) - Soft Rock hole | No | 7
2.25 | Excavate 600mm deep trench on tar surface | m³ | 1.8
2.26 | Bedding under and filling around cables comprising sifted sand | m³ | 0.9
Assemble and Install 3-Phase LV Structures for overhead ABC conductor
2.27 | Supply and Install Strain Assembly (60-90) degree bend | No | 2
2.28 | Supply and Install Terminal Assembly | m | 2
Stay Wire Assembly
2.28 | Supply and install LV stay wire assembly | No. | 4
Generator Fencing
2.3 | Herbicide/Insecticide application | m² | 24
2.31 | Supply, lay 25mm - 40mm yard stone and clean all weeds | m³ | 5
2.32 | Construct 1.8m high ClearVu fencing installed complete | m | 20
2.33 | Supply and install 2m wide ClearVu sliding gate complete | No. | 1
2.33 | Remove and re-instate tar | m² | 20
Testing and commissioning
2.34 | Factory Acceptance Tests ( FATs ) on the generator, before delivery to site, to confirm adherence to specifications - testing equipment to be provided by the contractor | Item | 1
2.35 | Test and commission the complete generator installation in the presence of the Consulting Engineer. This should be done in line with the specifications and the generator manufacturer's recommendations. The contractor to provide complete and detailed test results and test certificate. | Item | 1
2.36 | Provide sufficient fuel and lubricants to allow for full testing and commission, to the full satisfaction of the Client and the Engineer | Item | 1
TOTAL CARRIED FORWARD TO SUMMARY PAGE
BILL 3: ADDITIONAL ITEMS
Provisional Sums
4.1 | Provisional amount for the Automatic Generator power and Municipal power inter-lock system as required. | Sum | 1 |  | 25000
4.2 | Provisional amount for the refurbishment/replacement of the existing kiosks as may be required. | Sum | 1 |  | 20000
Documentation
4.3 | Provision of the Certificates of Compliance as per the requirement of SANS 10142-1 upon completion for the electrical works covered within the contract. | Item | 1
4.4 | Provision of the Operation and Maintenance manuals for the works covered within this contract including product warrantees, and product brochures (3 sets - 1 original and 2 copies). | Item | 1
Training
4.5 | Conduct Training for the Client User's personnel | Item | 1
Guarantee
4.6 | 12 month equipment and installation guarantee on the works covered within this contract.The guarantee period commences on the day of successful handing over of the building to the Client | Item | 1
TOTAL CARRIED FORWARD TO SUMMARY PAGE
Item | Description |  |  | Page No. | Amount
SUMMARY PAGE
5.1 | BILL 1: PRELIMINARY & GENERAL ITEMS |  |  | 1
5.2 | BILL 2: 110kVA STANDBY GENERATOR INSTALLATION |  |  | 4
5.3 | BILL 3: ADDITIONAL ITEMS |  |  | 8
5.4 | 10% CONTINGENCIES
SUB-TOTAL (Excluding VAT)
Add VAT @ 15%
GRAND TOTAL (Including VAT)
NOTE: ALL RATES AND PRICES EXCLUDE 15% VAT and CONTIGENCIES
Contractor's Name
Electrical Contractor’s Registered Person's Number (Wireman's License)
Name of Registered Person
NB: Only contractors whose Registration with the Department of Labour is for Three Phase installations will be considered.
MINIMUM CIDB GRADING OF 2EB IS REQUIRED
Signature of person authorised to sign the tender: ……………………………………………………………